SECTION XXXXX

PUMP STATION CONTROL PANELS

PART 1 GENERAL

  - SECTION INCLUDES

- This section includes all elements required to furnish and install a complete electrical control system to control, operate, and display information as indicated in the plans and specifications. The control system shall include all equipment, devices, wiring, and incidental materials to operate the system and display or relay information in accordance with these specifications. The intention of this section is to secure a complete control system that will operate equipment in accordance with narratives and requirements indicated in the plans, specifications, and manufacturer's literature for the equipment installed. All circuits and devices for protection of installed equipment shall be included in the lump sum bid.

  - SCOPE OF WORK

- The contractor shall furnish and install with each pump station, one EcoSmart AB Station® control panel.  The pump station control panel shall house the complete electrical system to operate the pump station. The control panel shall be manufactured by a UL certified panel facility and shall meet all UL698A standards (Industrial control equipment with circuit extensions into hazardous locations).  All components shall be UL recognized or listed including those supplied by the pump manufacturer and the control panel shall house all necessary controls including circuit breakers, VFD’s, and other equipment specified herein.  The panel shall be built to meet NEMA Type 4X ratings (Controls compartment), NEMA Type 3R ratings (Service and MCC compartments), and shall in all respects conform to the National Electric Code and all other state and local codes which may apply.

  - DEFINITIONS

- AIC – Amps Interrupting Current is the maximum current that is produced upon a fault to ground or a fault between phases.

- Arc Flash – An electrical explosion that can occur when there is an uncontrolled conduction of electrical current to ground or to another phase.  An Arc Flash occurs very rapidly and produces intense heat and energy that can harm personnel and destroy equipment.

- Control Compartment – A compartment in the EcoSmart AB Station® that contains all control components of the pump station including the Micrologix 1400® PLC, PanelView Plus HMI, communications and other devices.

- ECO Mode – An operation mode that operates the pumps at a speed determined by auto efficiency tuning of the controller.

- FLA – Full Load Amps

- GFCI – Ground Fault Circuit Interrupter

- GPM – Gallons Per Minute

- HMI – Human Machine Interface

- HOA – Hand-Off-Auto operator switch

- kW – Kilowatts (power)

- MCC – Motor Control Center

- MCC Compartment – A compartment in the EcoSmart AB Station® that contains components related to motor starting.  Some components include variable frequency drives, pump breakers, the control power transformer, and the voltage monitor.

- Service Compartment – A compartment in the EcoSmart AB Station® that contains service entrance equipment for the station.  Some components include main incoming terminal blocks, main service circuit breaker, phase monitor and other protective devices, and a transfer switch with generator receptacle (if required).

- PID – Proportional Integral and Derivative

- PID Mode – A mode in the controller that keeps a constant wet well level by varying the pump speed.

- PLC – Program Logic Controller

- Skirt Compartment – A vented compartment under the EcoSmart AB Station® that is reserved for routing of cables into various compartments.

- UPS – Uninterruptable Power Supply

- VFD – Variable Frequency Drive

  - REFERENCES

- ANSI®/NFPA® 70 – National Electrical Code® (NEC®)

- IEC 61000 – Electromagnetic Compatibility

- NEMA 250 – Enclosures for Electrical Equipment

- NEMA ICS7 – Industrial Control and Systems Adjustable Speed Drives

- UL® 50 – Enclosures for Electrical Equipment

- UL 98 – Disconnect Switches

- UL 507 – Electric Fans

- UL 508 – Industrial Control Equipment

- UL 508C – Power Conversion Equipment

- UL 698A – Circuit extension into hazardous locations

- UL 991 – Safety Tests

- IEEE-519 – Harmonic levels

- NFPA 70E – National Fire Protection Association

  - SUBMITTALS

- The Engineer reserves the right to approve or disapprove any and all equipment based upon evaluation. Approval for fabrication and installation will be made only after submittal and review of all shop contract documents. The information required for approval shall include the following items and be provided to the engineer prior to the bid date.

- Electrical schematics

- Enclosure dimensional drawings

- Complete layout drawing with dimensions

- Heat loss calculation in MCC compartment

- Manufacturer data sheet for all components

- Complete bill of material

- User operating manual

- Installation instructions

- 2 year warranty certificate

  - SUBSTITUTIONS

- The Engineer will consider proposals for substitution of materials, equipment, methods and services only when proposals are accompanied by full and technical data and all other information required by the Engineer for the proposed substitution.  Substitution of materials, equipment, methods and/or services is not allowed unless such substitution has been specifically approved by the Engineer.

  - QUALITY ASSURANCE

- Enclosure

- The enclosure shall be fabricated under the regulations of ISO 9001 certification for the manufacturing of enclosures.

- The enclosure shall be a UL508 listed enclosure.

- Control panel

- Control panel shall be manufactured in a UL508A facility and be UL certified to manufacture panels with UL698A intrinsically safe components.

- Factory shall conduct full operational tests with appropriate voltage applied to the panel.

  - DELIVERY, HANDLING, STORAGE

- All materials relating to this section individually and as completed panels shall be handled as fragile equipment and stored only inside closed buildings and protected from moisture entry. All openings shall be continuously sealed until the moment that connections thereto are actually made.

  - WARRANTY

- Warranty: 24 Months from date of manufacture. The warranty shall apply to being free to defects in material and workmanship.

PART 2 PRODUCTS

  - ENCLOSURE

- The enclosure shall be one freestanding enclosure consisting of four different compartments within one footprint.  Approved Enclosure shall be Arc Armor® by PRIMEX, an SJE Rhombus master brand.

  - COMPARTMENT REQUIREMENTS

- The Service compartment shall be a NEMA Type 3R rated compartment that houses the main 	service power components.

- The MCC compartment shall be NEMA Type 3R rated compartment that houses the motor starter components.

- The Control compartment shall be NEMA Type 4X rated compartment the houses all controls 	associated with the panel.  The maximum voltage within this compartment is to be 120vac.

- The Skirt compartment is a nonrated vented compartment that provides an area for the entry of well conduits.  All conduits with the exception of line power will come through the Skirt compartment.

- Conduit and mounting template – A drawing shall be provided with each enclosure to provide anchoring locations and conduit locations entering the enclosure.  This drawing shall be available at the time of conduit and foundation layout.

  - ENCLOSURE CONSTRUCTION

- All compartments are fabricated as one complete unit with singular common separation walls resulting in one complete enclosure.  The NEMA Type rating integrity of each compartment shall be maintained at all times from the factory manufactured enclosure through final installation.

- The entire panel enclosure shall be fabricated with stainless steel type 304 (18-8 stainless 18% chromium, 8% nickel)

- Welding requirements: stainless steel shall be welded using type "L" (low carbon) type welding rods during fabrication.

- Interior wall construction: all common walls shall consist of one sheet of type 304L (18-8) 	stainless steel with a minimum 14-gauge thickness (0.075 inches).  Backs to back or double 	walls are not acceptable.

- Interior mounting: all mounting plates, hinges and other components mounted onto the enclosure walls shall be held in place by welded in place stainless studs.  There shall be no penetrations for through bolts or other means of anchoring into the compartments from the exterior of the cabinet.

- Threaded studs: all studs shall be stainless flanged weld stud, with AISI Grade 304/305 standard steel, tensile strength = 85,000 psi, yield strength = 40,000 psi (of the stud, not the welded interface), un-plated surface. Sizing = 10 x 32, ¼ x 20.  All nuts shall be of the same quality.

- The exterior and interior finish of the panel shall be powder coat 3-4 mil minimum polyester power coat finish.  The enclosure shall be prepped by an acid wash prior to an electro-statically precipitated applied paint that should be baked at a high temperature to bond paint to enclosure surface.  Powder coating shall be performed after final enclosure assembly and prior to mounting electrical devices and components. All surfaces shall be painted on both sides and on edges.

- Exterior door handles to be die-cast aluminum alloy powder coated black.  Door handles to be fully lockable and able to accommodate a #21 Master padlock.  Each door handle must be NEMA Type rated to maintain the rating of the associated compartment.

- Exterior door hinges shall be continuous 304L stainless steel piano type hinges. All hinges are finished with white powder coating.

- Mechanical door stops to be mounted on the Control and MCC compartment doors to secure the door in the open position at 110 degrees.   Door may be closed by manually lifting up on the door stop arm.  They shall be located at the bottom of each cabinet door.

- A grey thermoplastic data pocket is to be mounted on the door of the MCC compartment.

- Two lifting eyebolt rings shall be installed on the top center of the panel and penetrate through the top of the panel.  The lifting eyebolt rings shall enter into the MCC compartment, not the Control compartment.  Each individual lifting eyebolt ring shall be rated the entire weight of the panel.  The top drip cap shall be structurally reinforced for the lifting load at the point of attachment of the eyebolt rings.  The lifting eyebolt ring shall have a gasket to prevent water entry into the MCC compartment.  Lifting eyebolt ring shall be oriented in parallel to the width of the enclosure.  They shall be constructed from high tensile strength steel, powder coated white.

- A drip cap shall be installed as one continuous sheet of stainless steel covering the entire top of the Arc Armor® enclosure.  The drip cap shall have rolled edge with a 1” trough continuous to each end.  It shall be constructed of a minimum 14 gauge stainless steel with a white powder coat finish.

- Back panels shall be constructed of polished aluminum, .125” thick minimum.  Back panels to have ¾” rolled edge flange with ½” mounting hole at a minimum at each corner.  Back panels are to be mounted to the enclosure with a minimum of 3/8” studs and nuts.  Back panels that are larger than 1200 square inches shall be constructed of white painted steel.

- The Control compartment shall have a dead front inner door for mounting the controller, indicators, and switches.  The inner door shall be constructed out of .125” aluminum.  The door shall be mounted to the enclosure via a continuous piano hinge.  Two twist lock latches are to be used to secure the inner door in the closed position.  The latches are to be T-handle type constructed from polyamide-6 nylon plastic 30% glass reinforced material.  They shall be mountable through square holes to prevent rotation of the entire mechanism

  - GENERAL ENCLOSURE REQUIREMENTS

- The reduction of the Arc Flash potential shall be reduced by isolating high voltage into specific compartments.

- The Service and MCC compartments may contain components that operate at a voltage that is capable of creating an Arc Flash condition. Personnel Protection Equipment (PPE) is required.  Accessibility should be limited to qualified electricians only.

- The Control compartment only contains control voltage (maximum of 120vac).  Minimal Personnel Protection Equipment (PPE) is required for operators and maintenance personnel.  See NFPA 70E for proper PPE requirements.

- All penetrations through compartments shall be performed to maintain the NEMA Type ratings of each individual compartment.

- The enclosure shall be constructed so that no screws or bolt heads are visible when viewed from any external portion of the enclosure.

- Punch cutouts for instruments and other devices shall be cut, punched, or drilled and smoothly finished with rounded edges.

- No holes shall be drilled in the top (rain cap) of the cabinet (with the exception of the lifting eyebolts).

- Electrical schematic shall be permanently affixed to inside of the outer door of the Control and MCC compartments. The schematic shall resist water to prevent removal and discoloration from heat, gasses, and ultraviolet light.

2.05 SERVICE COMPARTMENT COMPONENT AND REQUIREMENTS

- Main service entrance termination

- The main service entrance conductors shall be terminated onto lugs mounted at the bottom center of the Service compartment.  The lugs shall be aluminum compression type and shall be rated for both aluminum and copper wire terminations.  The lugs shall be sized to accommodate the wire size of service entrance conductors.

- Component shall be Allen Bradley, bulletin 1492.

- Main Circuit Breaker

- The main circuit breaker shall be a thermal-magnetic molded case circuit breaker rated to 600V and sized according to the NEC and the load requirements of the control panel.  It shall be mounted in the compartment with a lockable handle mechanism mounted on the Service compartment door.

- Component shall be Allen Bradley, bulletin 140U

- Surge Arrestor

- A surge arrestor shall be connected to the load side of the main service circuit breaker.   It shall be mounted behind a protective cover on which the main service entrance termination lugs are mounted.

- Components shall be Delta, Model LA603

- Surge Capacitor

- A surge capacitor shall be connected to the load side of the main service circuit breaker.   It shall be mounted behind a protective cover on which the main service entrance termination lugs are mounted

- Component shall be Delta, Model CA603R

- Phase Monitor

  - The phase loss monitor shall be supplied from the load side of the main disconnect.  It shall monitor the voltage of each phase and provide a dry contact closure upon phase loss, phase reversal, overvoltage or under voltage condition. Monitor shall have an adjustable reset delay

  - Component shall be SYMCOM, 460

- Generator receptacle

- An optional generator receptacle shall be mounted on the side of the Service compartment for control panels equipped with manual transfer switch. The receptacle shall be of reverse service configurations to avoid exposure to live parts when the mating plug is energized.

- Component shall be manufactured by Crouse Hinds and/or match existing site generator plug style.

- Generator Main Circuit Breaker

- If a generator receptacle is installed, it is to have a designated Main Circuit Breaker that is mechanically interlocked with the Line Main Circuit Breaker.  The mechanical interlock must prevent both breakers from being in the ON position at the same time

- The generator main circuit breaker shall be a thermal-magnetic molded case circuit breaker rated to 600v and sized according to the NEC and the load requirements of the control panel.  It shall be mounted in the compartment with a lockable handle mechanism mounted on the Service compartment door.

- Component shall be Allen Bradley, Bulletin 140U

  - MCC COMPARTMENT COMPONENT AND REQUIREMENTS

- 3-Phase voltage indicator

- A voltage indicator shall be mounted on the door of the MCC compartment to provide a warning that high energy circuits are energized and voltage is present on each phase.  The voltage indicator warns against the potential danger of electric shock, Arc Flash and/or Arc Blast conditions inside the cabinet.

- Component shall be Diversified Electronics, Model UPA-10

- Door interlock

- An electromechanical door interlock shall prevent access into the MCC compartment unless the main power is disconnected.  The MCC compartment door interlock mechanism is powered through a two-pole circuit breaker in the MCC compartment.

- Component shall be Hoffman, Model AEK460NDH-460

- Pump circuit breakers

- Pump circuit breakers to be a thermal-magnetic molded case breaker.  Individual pump circuit breaker shall be sized according to the VFD manufacturer, NEC and the FLA of the pump.

- Components shall Allen Bradley, bulletin 140U

- Control transformer primary circuit breaker

- The control power circuit breaker shall be sized according to the rating of the primary windings of the control power transformer.  The line side of the circuit breaker shall be supplied from a tap from the load side of the main circuit breaker.  It shall be DIN rail mounted and adjacent to the MCC Compartment door interlock circuit breaker.

- Component shall be Allen Bradley, Bulletin 1489

- Door interlock circuit breaker

- MCC compartment door interlock circuit breaker shall be a two-pole 10-amp circuit breaker and supplied from a tap from the load side of the main circuit breaker. It shall be DIN rail mounted and adjacent to the control power circuit breaker.

- Component shall be Allen Bradley, Bulletin 1489

- Control power transformer

- A control power transformer is only required on stations that do not provide 120 volts to a service neutral.

- Component shall be Hammond, PH1500MQMJ-FK

- Line reactors

- A line reactor shall be connected to the input of each VFD power circuit. The line reactor shall be located in the MCC compartment and selected according VFD manufacturer and the motor FLA.  One line reactor shall be installed per VFD to provide a reduction of harmonics.

- Component shall be Allen Bradley, bulletin 1321

- Variable Frequency Drives

- VFD’s shall be located in the MCC compartment and connected to the load side of a dedicated line reactor.

- VFD requirements are to follow specification as stated in this Section 2.10.

- Cooling fans

- The MCC compartment shall have two ventilation fans.  One fan shall be located at the air intake shroud in the bottom right side of the compartment, supplying air into the compartment.   A second fan shall be located at the exhaust shroud, located in the upper left side of the compartment and exhausting air outside. Both fans shall 120VAC supplied from 3-amp circuit breaker and be thermostatically controlled. Each fan shall have filter and finger guards.

- Components shall be Sunon, P/N-SP100A

- Thermostat

- A thermostat shall be mounted in the MCC compartment and operate the fans on rising internal temperature.  The thermostat shall be mounted in the lower half of the MCC compartment in order to avoid short cycling.  The thermostat shall control the operation of both fans in parallel.

- Component shall be Pfannenberg, P/N-17121000010

- Compartment Service Light

- The MCC compartment shall have an LED service light installed in the upper front portion of the compartment. The service light shall be operated by an ON/OFF switch located on the inner door of the controls compartment. It shall operate at 24VDC and be supplied from the battery backup in order for the light to operate during a power loss.

- Component shall be Super Bright LEDs, LF-CW30SMD

- Pump Terminal Blocks

- The terminal blocks for motor lead terminations shall be mounted on an angled and raised bracket to provide easy access for field wiring terminations.

- Components shall be by Allen Bradley, (size will very on pump size)

- MCC/Control compartment interconnecting seal barrier

- A cable barrier shall be installed that provides isolation between the MCC compartment and the Control compartment.  The barrier shall be used to maintain a NEMA Type 3R rating in the MCC compartment and a NEMA Type 4X rating in the Control compartment.  All control cables shall pass through the barrier.

- Component shall be ROXTEC, P/N- EZ00000001010

2.07 CONTROLS COMPARTMENT COMPONENT AND REQUIREMENTS

- PLC controller

- The controller shall be comprised of two components. An HMI display unit mounted on the inner door and PLC mounted on the back plate.  The two are connected via an Ethernet switch.

- The HMI shall have the following features:

- 6.5 inch color touch screen

- Color active-matrix TFT

- Resolution: 640 x 480, 18-bit color graphics

- Luminance: 300 cd/m2 Nit

- Ethernet communications

- 2 serial RS 232/RS485 isolated ports

- Secure Digital (SD) card, supported by hot-swappable SD card

- Component shall be Allen Bradley PanelView Plus 2711P-T7C4D8

- The PLC module shall have the following features:

  - 12 digital Fast Inputs 24VDC

  - 8 digital Normal Inputs 24VDC

  - 6 relay outputs

  - 3 Fast DC output

  - 3 normal DC output

  - 4 analog inputs (V)

  - 2 Analog output (V)

  - Real Time Clock

  - Embedded LCD display

  - Serial and Ethernet communications ports

Component shall be Allen Bradley Micrologix 1400, 1766-L32BXBA

- DC Power Supply/UPS

- The power supply shall have the following characteristics:

  - Input voltage: 100 to 240Vac

  - Output power 240 watts

  - 24V to 28VDC output Voltage

  - 24VDC, 10A max output current rating

Components shall be Allen Bradley 160-XLS240E

- The uninterrupted  power supply shall have the following characteristics:

  - Output 240 watts

  - 22.5 to 30VDC input Voltage

  - 24VDC, 15A max output current rating

Components shall be Allen Bradley 160-XLS240-UPS

- Battery

- The battery backup power shall consist of two 12 VDC batteries configured in series to provide an output voltage of 24 VDC.  The batteries shall have a minimum rating of 7 amp hours.

Component shall be Allen Bradley 1606-XLSBATASSY1

- Over Temperature and Seal Fail Monitoring Relay

- The relay shall be compatible with the pump that is installed in the wet well.

- There shall be one relay per pump that is present in the system.

- The relay shall have the following requirements:

  - Molded relay bezel to allow for door mounting.

  - Power on light.

  - Over temperature and Seal Leak fault light.  Color: Red.

  - Selector switch for Auto or Manual mode.  This switch shall allow the user to select between automatic or manual reset of the heat sensor fault.

  - Provide an over temperature reset pushbutton for Manual reset mode.

  - Seal fail sensibility to be adjustable between 4.7K ohm to 100K ohm via an adjustable potentiometer.

- Default component shall be PRIMEX, Model PMR-1

- Intrinsically safe barrier

- The intrinsic safety barriers shall be DIN rail mounted and located in a UL approved isolated Safety Barrier location.   The intrinsic safety barriers shall be used to limit the amount of energy available to all level sensing circuits in the wet well in order to prevent sparking.

  - Analog IS barrier

    - Allen Bradley, Model  897H-S214

  - Back up float switches IS barrier

    - Allen Bradley, Model 897H-G231

- Control circuit breakers

- The control circuit breakers shall be located in the Control compartment and used to protect all 120 volt and 24 volt circuits.  The 120 volt circuit breakers shall be supplied by the secondary side of the control transformer (unless 120 volts is available from the main electrical service).

- There shall be six single pole control circuit breakers as follows:

  - Main control power

  - Fan

  - GFI Receptacle

  - Heater

  - Control wiring

  - 24vdc Power supply

- Components shall be Allen Bradley bulletin 1489

- Control Relays

- Control relays shall have the following characteristics:

- 4 pole, 7A,

- Coil: 120 VAC or 24 VAC

- DIN rail mounting

- Terminal screw type socket

- Pilot light indicating status

- Manual operator

- Protection module mounted in base (diode, RC circuit or varistor)

- Metal hold down clip

- Components shall be Allen Bradley 700-HC

- Anti-condensation heater

- A compartment heater shall be supplied and mounted at the bottom portion of the Control compartment.  The heater shall be positioned away from any heat sensitive components directly above the heater. Construction should be vulcanized fiberglass-reinforced silicone rubber encapsulating a nickel alloy heating element with an integrated thermostat.

- Component shall be ElectroFlex, Model EN2-125

- Compartment Service Light

- The controls compartment shall have an LED service light installed in the upper front portion of the compartment. The service light shall be operated by an ON/OFF switch located on the inner door of the controls compartment. It shall operate at 24VDC and be supplied from the battery backup in order for the light to operate during a power loss.

- Component shall be Super Bright LEDs, LF-CW30SMD

- Utility receptacle

- A GFCI receptacle shall be mounted on the Control compartment inner door.  The receptacle shall be rated at 15 amps, but restricted to 7 amp service by a dedicated 10 amp 120 VAC circuit breaker.  The circuit breaker shall be supplied from the secondary of the control transformer.

- Component shall be Leviton, Model 75991

- Selector Switches

- Switches shall be mounted on the Control compartment inner door.  The switches shall have extended operator handles.

  - HOA Switches

    - There shall be a HOA selector switch for each individual pump.  When in Hand, the pump shall run at a preset speed.  In the Off position, the pump will neither run in the auto or manual mode.  When in Auto, the pumps will cycle per the commands of the PLC.

    - Components shall be Allen Bradley 800F series

  - ON-OFF Switch

    - There shall be a ON-OFF selector switch to allow the operator to turn on and off the cabinet lights.  This switch is to be mounted on the inner door.

    - Components shall be Allen Bradley 800F series

- Indicator Lights

- Alarm lights shall be mounted on the Control compartment inner door.  There shall be two alarm lights; High-Level light with a yellow lens, and a Low-Level light with a yellow lens.

- The pilot lights shall be 22 mm in diameter 24Vdc.

- Components shall be Allen Bradley 800F series

- Push Buttons

- An alarm test button shall be mounted on the Control compartment inner door.  The alarm test button activates both the horn and strobe light to ensure proper operation.

- An alarm silence button shall be mounted on the side of the enclosure below the horn/light assembly.  When pressed, the silence button will silence the audible alarm.  The audible alarm will latch in silence mode until all alarms are reset and there are no longer any alarm conditions.

- Components shall be Allen Bradley 800F series

- Audible and Visual Alarm

      - An alarm horn and red strobe beacon shall be mounted on the outside of the Control compartment and be activated on High-level or common alarm from the PLC.  If the audible is silenced, the alarm light will continue to flash until the alarm condition is cleared.  The red strobe beacon should be mounted in a way that it is visible from 180 deg. around the panel.

        - Voltage shall be 24Vdc. and operate on the UPS power circuit in case of main power fault.

        - The horn and light assembly shall be sealed as one part from the manufacture and be rated at NEMA Type 4X.

        - Lens Color: Red

        - Horn to be a minimal of 100dB

      - Components shall be Allen Bradley, 855F-VMSC20B24L4P1

- Submersible Level Transducer

- One analog submersible level transducer shall be supplied with the control panel.  The transducer shall have the following characteristics:

  - 4-20 milliamp level signal

  - Sealed unit, non fowling

  - Flush Kynar diaphragm

  - Abrasion resistant

  - Built in lightning arrestor

  - Lifetime warranty

- Component shall be Keller America, Model Level Rat

- Back up float switches

- Two mechanical control float switches shall be supplied with the control panel in order to operate the backup float circuitry.

- Component shall be PRIMEX PMA.

2.08 SEQUENCE OF OPERATION

- General

- The pump program shall run on the Micrologix 1400 PLC and PanelView HMI color touch screen.  The pump program does not require any tools or laptop computer to configure.  All configuration and setup shall be achievable from the menus on the touch screen display.  The LED backlight of the HMI shall be dimmed off as the door of the control compartment is closed to save energy and to maximize the battery autonomy during power failure

- Level Monitoring and Control

- The wet well level shall be monitored on the main screen in feet and tenths of feet. A setup screen shall enable the user to set the span and offset of the level transducer. A level setup screen shall be available for the user to set the five level set points required for a duplex lift station:  Low level alarm, Stop all pumps level, Start lead pump, start lag pump & high level alarm.  A level simulation function shall also be available for the operator to manually raise and drop the level of the wet well from the touch screen without handling the level transducer.  The simulation function shall be self terminating after 5 seconds on inactivity to prevent the user from leaving the station in the level simulation mode.

- Pump Operation

- The pump program shall monitor the position of each pump HAND/OFF/AUTO selector switch.  Only pumps in the AUTO mode shall be called to run in automatic pump operation. In HAND mode the pump shall run irrespective of the status of the controller and the wet well level.  In the HAND position the selection switch shall directly control the VFD run command and speed control. In AUTO mode, the pump operation shall be based on the level of the wet well and the level set points.  As the level of the wet well rises above the “Start lead pump level” the lead pump shall start and run continuously until the level drops below the “stop all pump level”.  When the level is below the “stop all pumps level” no pump shall run in AUTO mode. As the level rises above the “Start lead pump level” again, the next available pump shall start and run continuously until the level drops below the “Stop all pumps level”.  Should the level continue to rise after the lead pump has started and reach the “start lag pump” level, the second available pump shall start and run simultaneously with the lead pump until the level drops below the “Stop all pumps level” and both pumps shall stop.  Should the level rise above the “high level alarm” setpoint, the alarm will sound and the strobe will turn on.  If the level drops below the “high level alarm” setpoint, the horn and strobe will stop, but alarm shall remain in the alarm log.

- Flow Monitoring

- The discharge flow rate of each pump shall be monitored by level changes in the wet well.  The controller shall be able to compute the flow rate base on fill time, discharge time, level changes and tank dimension.  The flow rate shall be updated at the end of each pump cycle and displayed on the main screen in GPM.  Flow monitoring shall be achieved without the use of a flow meter for cylindrical and rectangular tanks.  Should a flow meter be made available, an analog input on the controller shall be enabled and the analog input shall be calibrated on the screen to display the correct GPM values.

- Energy Efficiency Auto-Tuning

- The controller shall be able to combine the flow calculation in GPM and power monitoring from the VFD to produce a W/GPM value after every pumping cycle.  This value represents the amount of energy needed to pump a gallon of liquid.  The ECO f(x) function shall perform an automatic speed search to find the pump speed that shall produce the lowest W/GPM.  This speed search shall be performed through the auto-tune algorithm found on in the ECO menu.  Once this speed is found, the pumps shall be operated at this speed during every cycle unless a high in-flow condition should occur.

- Proportional, Integral and Derivative (PID)

- During high in-flow condition, the controller shall automatically switch from cycle based operation to PID (constant level) operation for maximum energy savings.  Three PID modes shall be available:

  - PID OFF:  Cycle based operation only

  - PID AUTO:  Automatic switching from Cycle to PID on high in-flow condition

  - PID ON: PID operation is always on

- Back Up Float System

      - Should the communication between VFDs and controller fail, the VFDs shall operate the pumps @ 100% (“Fallback speed”) when called to run.  An alarm shall be issued.

      - Should the level transducer fail, the float switch backup system shall take over.  An alarm shall be issued.

      - Should the PLC fail, the pump operation shall be based on the back up float switches.  Should the High Level float switch alarm activate, both pumps shall run at full speed until low level float switch is reached.  An alarm shall be issued.

- Communications

      - The PLC shall be able to communicate via the following methods:

        - Dial up modem (RS 232 or Ethernet)Radio modem (RS 232 or Ethernet IP)

        - Cellular modem (RS 232 –to modem to GPRS to TCP/IP)

2.09 HMI Screens

A.  Main Screen Description

      - The main screen shall display the most commonly required information regarding the operation of the pump station.  The following items are displayed:

        - Pump run status

        - Pump speed (Hz)

        - Pump current (Amps)

        - Pump discharge flow (GPM)

        - Wet well level (feet)

        - Station Inflow (GPM)

        - Efficiency - Watts per GPM (energy use)

        - Total Volume pumped

        - Pump Cycle counter

        - Pump total hours run

        - Station status bar

        - Fault (high level alarm)

        - High Float alarm at top of display

        - Auto / Manual

        - ECO mode

        - PID control

        - Best Efficient Frequency operation (Hz)

B. Alarm Screen Description

    - The Alarm Menu display shall indicate the most commonly required information regarding the alarms at the pump station.  The Alarm Menu shall have the following features:

  - View current alarms

  - Sort by alarm date and time

  - Zoom into alarm providing more details

  - Alarm history (256 previous alarms

C. Menu Display Description

- The Navigation menu shall not be password protected.  It shall allow navigation to the 	following displays:

  - Alarm Menu Display

  - Data Log Display

    - Station Totals

    - Daily Totals

    - Trend Charts

    - Data Storage (SD card)

D. Setup Menu Description

- The setup menu displays shall require a password.  The setup displays are as follows:

e. LEVEL

f. VFD

c. SENSOR

d. P.I.D.

e. FLOW

f. ECO

g. COM

h. SYSTEM

E.  Level Setup Display Description

1. The wet well level display shall have the following characteristics:

        - Level set point setup

    - Low-level elevation

    - Stop pumps elevation

    - Start lead pump elevation

    - Start lag pump elevation

    - High-level elevation

  - Current Level indication

    - Input Status

  - Simulation Buttons

    - Simulation, Push and Hold

    - Will automatically return to actual level after 5 seconds of inactivity.

F. VFD Setup

      - The VFD setup display shall enable the operator to set the following functions:

  - Minimum and maximum speed allowable for pump operation

  - The maximum run time per cycle

  - Alternation (1-2/Auto/2-1)

  - Dry run protection

- Sensor Setup

- The sensor setup display shall enable the operator to set the level transducer zero and span in feet and tenths of feet.

- P.I.D. Setup display

- The PID setup display shall enable the operator to set the following functions:

  - Proportional gain

  - Integral Time

  - Derivative

  - P.I.D. controls mode (off/auto/on)

- Flow Setup

- The flow setup display shall enable the operator to set the following functions:

  - Flow calculation based on a cylindrical tank

  - Flow calculation based on a rectangular tank

  - Setup of flow monitoring of 4-20mA flow meter

- Eco-f(x) Setup display

- The Ecof(x) setup display shall enable the operator to set the following functions:

  - Enable/disable eco f(x) function

  - Initiate an efficiency auto-tuning sequence

  - Visualize the W/GPM for each frequency searched

  - Visualize the search result

  - Visualize the energy savings as compared to a conventional control system

- COM Setup display

- The communication setup display shall enable the operator to set the following functions:

  - Enable/disable SMS service

  - Setup phone numbers to be call during alarm conditions

  - Visualize VFD/Controller communication status

  - Enable/disable VFD/Controller communication

  - Setup GPRS communication

- System Setup display

- The system setup display shall enable operator to set the following functions:

  - Back to main screen timer

  - System time (real time clock)Password (setup access control only)

  - I/O status visualization

  - User programmable relay setup

- Help Menu description

- The help menu does not require a password.  The help menu shall provide detailed help information on the operation all displays and data entry requirements.

- Data log display description

- Station Totals

  - Total hours per pump

  - Kilowatt – hours

  - Kilowatts

  - AC Voltage

  - Pump data (manufacturer, model, HP, V, FLA)

- Daily Totals

  - Table and Graph format

  - View last 100 data of totals

  - Cycles

  - Run times

- Trend Charts

  - Live Trends

  - Scroll bar scrolls

  - Logs data every 5 minutes

i. Level

ii. Flow

iii. Amps

iv. Watt per GPM

2.10 VARIABLE FREQUENCY DRIVES

A. VFD Requirements

1. VFD’s shall be located in the MCC compartment and connected to the load side of a dedicated line reactor.  The VFD shall have the following characteristics:

a.  Be sized appropriately delivery sufficient current to the motor and not overload throughout the pump curve.

b.  Be size appropriately as provide sufficient cooling and not overheat when installed in the MCC enclosure.

c.  Be selected according to the manufacturer as to operate with the available incoming voltage and match the motor nameplate voltage.

d.  Be sized appropriately according to the manufacturer as to operate when only single phase incoming power is available.

f. Must support Ethernet IP communications for control and monitoring by the PLC

g. Must accept an external input from an HOA switch for manual run control at a pre-set speed.

h. Must accept an external input from the PLC as a run command.

i.  Operate from an input voltage frequency range of 47–63 Hz.

j.  The displacement power factor shall not be less than 0.95 lagging under any speed or load condition.

B. VFD Protection

1. The VFD shall have the following protective characteristics:

  - The VFD shall be protected against short circuits, between output phases and to ground.

  - The VFD shall have under-voltage and over-voltage protection.

  - The VFD shall provide class 10 motor overload protection investigated by UL, to comply with N.E.C. Article 430.

  - The VFD shall be able to sense a loss of load and signal a fault.

  - If the input analog reference is lost, this shall cause a warning to be issued and the user shall have the option of pre-selecting either (1) stopping and displaying the fault, (2) running at programmable preset speed, or (3) running at min or max frequency.

  - Upon VFD fault, drive shall store the DC bus voltage, out current and output frequency in readable parameters.

C. VFD Operator Interface

1. The VFD Operator Interface shall have the following interface characteristics:

- The VFD shall include an integral programming terminal.

- The programming terminal shall have at minimum a 2 line by 16 character LCD display with LED backlight.

- Digital speed control buttons shall be provided. Potentiometers are not acceptable.

- Programmable Hand-Off-Auto buttons shall be provided to toggle both start and frequency control or only the frequency control to and from the programming terminal.

- Text support in multiple languages, including but not limited to English, German, French, Italian, Spanish, Portuguese and Dutch.

D. VFD Manufacturer

1. VFD shall be Rockwell Automation – Allen Bradley Powerfex 400 series (size according to manufacturer)

PART 3 EXECUTION

3.01 GENERAL

A. 	All work shall be done in accordance with appropriate Divisions and Section and shall be 			performed in a workmanship manner.

3.02 FABRICATION

A.	All control panels shall be shop assembled and factory tested prior to delivery to the site. 				Final as-built drawing shall be made to reflect all adjustments and modifications made to 				the system after start-up has been completed satisfactorily. All equipment and devices 				shall be mounted, adjusted, calibrated, and operated exactly as recommended by the 				manufacturer of each component.

B. 	Control switches, indicator lights, and other devices shall be grouped as stated in this					section and in submittal package.

3.03 EQUIPMENT INSTALLATION

A. 	All equipment shall be installed in accordance with approved drawings and the manufacturer’s 				written instructions.

3.04 WIRING AND TERMINATIONS

A. 	All wiring shall follow NEC color coding scheme.

B. 	All wiring shall be run parallel to side walls of panels and/or in covered wiring troughs. Wires 				passing across hinged areas shall be protected by abrasion resistant cabling materials.

3.05 IDENTIFACATION

A.  	All conductors shall be labeled at each end with numbers matching submittals data sheets and all				wire terminations shall be identified by the component terminal numbers as shown on 					appropriate panel drawings.

3.06 START UP

  - Startup shall be done in accordance with manufacturer’s written instructions and be completed by qualified electrician or PRIMEX.

  - A completed start up report shall be returned to PRIMEX in order to maintain full warranty coverage.

END OF SECTION